## Sheet1
Template for I/A Tech Comparison
Category | KleanTu Submission 12-01-21
SFR - Single Family Residence (330 permitted gpd, 165 gpd flow for cost effectiveness calculations | ---------------------------------------------
Influent - Assume septic tank discharges at 65 mg/L TN and drainfield takes out another 25%, so 50 mg/L TN is reasonable baseline for comparisons. | ---------------------------------------------
Basics
Manufacturer / Parent Company | KleanTu® LLC (Edgartown, MA; Pittsburgh, PA)
Model / Technology Name | NitROE® Wastewater Treatment System Models: 2KS, 2KM, 10KM, SSD
Background
Patent Year | Pending
Years in production | Five (5) years
Approach
Category (Media filter, ATU, Membrane, sequencing batch reactors, drainfield, etc.) | Biological nitrification / denitrification in a media system
Positioning
Ideal applications | Applicable to single residences, apartments, townhouses, clusters of residences and commercial establishments
Capacity Range | 100 gpd to 1 million gpd or more (gpd = gallons per day)
Performance
TN concentration output range category (<5 / <10 / <15 /<19 mg/L) | Less than 10 mg/l
TP concentration output range category (<0.5/<1.0 mg/L) | Phosphorus removal an added feature if needed to reduce phosphorus concentrations in the effluent
kg N removed/year beyond Ref'd 50 mg/L | 73 lb/yr (33 kg/yr) based on Case History below
Approvals
Residential Permits | A number of Towns in Massachusetts
MA
General/ Provisional (<50)/Pilot (<10) | Provisional Permit
RI | ---------------------------------------------
Other States | ---------------------------------------------
Commercial Permits | MA DEP and Towns in Massachusetts
Testing
Internal performance testing data - how many years / data points / sampling frequency? | Five (5) years as of Nov 2021
Internal performance testing data - Range, mean, median BOD/TSS/TN values | Five (5) years as of Nov 2021
3rd party testing data - how many years / data points / sampling frequency? | Three (3) years as of Nov 2021
3rd party testing data - Range, mean, median BOD/TSS/TN/TP values | Case History - Single Family Residence 2KS Model (Average of 19 Months Sampling): Flow Rate 352 gallons per day Nitrogen In 73 mg/L Nitrogen Out 5 mg/L BOD5 Out 5 mg/L TSS Out 16 mg/L Nitrogen Removed 73 lb/yr
3rd party testing source/organization (s) | Massachusetts Alternative Septic System Test Center (MASSTC) Buzzard's Bay Coalition Envirotech Lab Barnstable County Health Lab
Cost
NEW SFR Construction (design+permit+equipment supply+install) | Average of multiple installations as of January 2020, $33,000 including septic tank and leach field excluding unusual site conditions and landscaping
Monthly operating costs (electricty etc.) | Single Family Residence 2KS Model: If not on solar panel, electricity cost is approximately $19 per month at $0.22 per kwh; adjust for other costs per kwh
Yearly O&M requirements
Yearly O&M costs (without sampling) | Single Family Residence 2KS Model: Approximately $595 per year in 2021 dollars including electricity, remote sensing and periodic repairs with replacement of parts and materials averaged over 20 years
Yearly O&M costs (with sampling) | For sampling add $275 per sampling event as required by locality (2021 dollars)
Expected system lifespan (range)
Total Cost of system over over 20 years (design + install + operation + maintenance + repairs) | Single Family Residence 2KS Model Retrofit: Approximate present value of $36,000 discounted at 5% over 20 years
Beyond 20 years | ---------------------------------------------
Cost Effectiveness
Cost per kg N removed beyond ref'd 50mg/L - 20 year | Approximately $25 per pound ($11 per kg) removed across NitROE 2KS based on Case History above at a single family residence for removal across NitROE tank
Beyond 20 years | ---------------------------------------------
Retrofits
Ability to use tech in retrofit applications | Can be retrofitted to existing septic systems
Expected capital cost of a retrofit for SFR | Around $25,000 (2021 dollars) for equipment and installation excluding unusual site conditions and landscaping
Phosphorus Removal
Commentary | Phosphorus removal can be added to any of the NitROE models for a modest increase in installation cost; phosphorus removal will add to operational costs in proportion to the amount of phosphorus to be removed and required effluent concentrations; disinfection can also be added to any of the NitROE models.
Pitch
Unique aspects/advantages | High-quality treated wastewater Simplicity (gravity flow, single air pump) Retrofit existing septic systems Out of sight integrated with landscaping; quiet without odors Remote sensing for real time monitoring of operation Green aspects Phosphorus removal and disinfection options Affordable
Why us? | High-quality treated wastewater with aesthetically-pleasing, simple system at affordable cost
Clusters
Cluster potential? | Models are available for treatment of clusters of single family residences
Range (gal/day) | Up to 1 million gallons per day or more
Contact Point
Local Representatives MA & RI | info@KleanTu.com and (800)303-4787